## Instructions for FORM WTG-1200
| Gas Operations and Maintenance Manual |  | Form WTG-1200 Rectifier Inspection Form Rev 2 - Dec 2022
When to Use This Form | This form packet is used to document inspection of rectifiers.
Reviewed Procedures
P-192.465(b) Inspect/Test/ Repair Rectifiers
P-192.465(c) Inspect Reverse Current Switches, Diodes,and Interference Bonds
P-192.483 Cathodic Protection Remediation
The applicable sections of the above procedure(s) shall be reviewed prior to completing this form.
Documentation Procedure
| 1. | Copy this form and return original to manual.
| 2. | Refer to Corrosion Control Procedures to ensure inspections are done correctly.
| 3. | Gather data and complete form. One section should be completed for each inspection (once every 2 months).
| 4. | If corrosion is found or there is a suspected need for remediation, document below and forward this document to the Corrosion Control Engineer for immediate review.
| 5. | Place completed form in file. Retain for the life of the line.
Form Version | Rev 2 - Nov 2022

## WTG-1200
[13 empty] | Form WTG-1200 Rectifier Inspection Form Rev 2 - Nov 2022 - Page 1 of 3 | [14 empty] | Form WTG-1200 Rectifier Inspection Form Rev 2 - Nov 2022 - Page 2 of 3 | [15 empty] | Form WTG-1200 Rectifier Inspection Form Rev 2 -Nov 2022 - Page 3 of 3
|  |  |  | Gas Operations and Maintenance Manual | [18 empty] | Gas Operations and Maintenance Manual | [14 empty] | Gas Operations and Maintenance Manual
| District | [12 empty] | System | [5 empty] | NOTE: | These data entry segments are only for rectifiers that service multiple structures | [13 empty] | NOTE: This page is for recording non O & M required data that is used for asset evaluation and management.
| Location | [12 empty] | Pipeline Name | [5 empty] | Read # | Negative/Drains |  |  |  | Read # | Negative/Drains |  |  |  | Read # | Negative/Drains |  |  |  | Ground bed watering procedure: Before adding water to bed, please record individual anode outputs. As
| County | [7 empty] | State |  |  |  |  | TRC/CC Unit | [5 empty] | 1 | Cir. | Description |  | Amp | 2 | Cir. | Description |  | Amp | 3 | Cir. | Description |  | Amp | water is added, please observe random outputs from anodes to ensure that they all are effectively watered.
[20 empty] | Found | 1 |  |  |  | Found | 1 |  |  |  | Found | 1 |  |  |  | Please also note in the remarks how much water was added. If watering a conventional bed, take note of the
| Please read information on page 3 of this form | [18 empty] | Left |  |  |  |  | Left |  |  |  |  | Left |  |  |  |  | output of the farthest anode to ensure total bed watering. Please include any problems in the remarks.
[20 empty] | Found | 2 |  |  |  | Found | 2 |  |  |  | Found | 2
| Manufacturer | [7 empty] | Rectifier ID/Name | [10 empty] | Left |  |  |  |  | Left |  |  |  |  | Left |  |  |  |  | Remarks/Comments:
| Model No. | [5 empty] | Power Vendor | [12 empty] | Found | 3 |  |  |  | Found | 3 |  |  |  | Found | 3
| Serial No. |  |  |  |  | Acct # |  |  |  |  | KWH Meter # | [5 empty] | KWH Reading |  |  | Left |  |  |  |  | Left |  |  |  |  | Left
| DC Volts |  |  |  |  | AC Volts |  |  |  |  | Max Coarse |  |  |  |  | Shunt mV/Shunt Factor |  |  |  | Found | 4 |  |  |  | Found | 4 |  |  |  | Found | 4
| DC Amps |  |  |  |  | AC Amps |  |  |  |  | Max Fine |  |  |  |  | Factor not in drop down |  |  |  | Left |  |  |  |  | Left |  |  |  |  | Left
| GPS Coordinates |  |  |  | Latitude |  | N | [5 empty] | Longitude |  | W |  |  |  |  | Found | 5 |  |  |  | Found | 5 |  |  |  | Found | 5
| RMU Type | [9 empty] | RMU Serial No. | [8 empty] | Left |  |  |  |  | Left |  |  |  |  | Left
[15 empty] | Ground bed type (deep or surface) |  |  |  |  | Should equal rect. Amps |  |  | Total | 0 | Should equal rect. Amps |  |  | Total | 0 | Should equal rect. Amps |  |  | Total | 0
| Important!! | [8 empty] | If no adjustments are made then only use the 'As Left' row | [9 empty] | Read # | Negative/Drains |  |  |  | Read # | Negative/Drains |  |  |  | Read # | Negative/Drains
| Separate drains/individual negative leads should be recorded on Page 2 - Mandatory for every meter read cycle | [18 empty] | 4 | Cir. | Description |  | Amp | 5 | Cir. | Description |  | Amp | 6 | Cir. | Description |  | Amp
Read | Technicain |  |  |  | Date |  |  | Test | [5 empty] | Taps |  | Actions? |  |  | Nearby | Found | 1 |  |  |  | Found | 1 |  |  |  | Found | 1
[8 empty] | Volts |  | Amps |  | Ohms |  | C | F | Comments |  |  | P/S= | Left |  |  |  |  | Left |  |  |  |  | Left
1 | [19 empty] | Found | 2 |  |  |  | Found | 2 |  |  |  | Found | 2
[20 empty] | Left |  |  |  |  | Left |  |  |  |  | Left
2 | [19 empty] | Found | 3 |  |  |  | Found | 3 |  |  |  | Found | 3
[20 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | Individual anode output records
3 | [19 empty] | Found | 4 |  |  |  | Found | 4 |  |  |  | Found | 4 |  |  |  |  | J-Box Shunt Factor
[20 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [9 empty] | Note: | Anode J box shunts are almost always .01 Ohm or 50mV=5A
4 | [19 empty] | Found | 5 |  |  |  | Found | 5 |  |  |  | Found | 5
[20 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | Anode Junction Box |  |  |  | Anode Junction Box |  |  |  | Anode Junction Box |  |  |  | Anode Junction Box
5 | [19 empty] | Should equal rect. Amps |  |  | Total | 0 | Should equal rect. Amps |  |  | Total | 0 | Should equal rect. Amps |  |  | Total | 0 |  |  | Date: |  |  |  | Date: |  |  |  | Date: |  |  |  | Date:
[20 empty] | Read # | Negative/Drains |  |  |  | Read # | Negative/Drains |  |  |  | Read # | Negative/Drains | [5 empty] | Cir. | Amp | Cir. | Amp | Cir. | Amp | Cir. | Amp | Cir. | Amp | Cir. | Amp | Cir. | Amp | Cir. | Amp
6 | [19 empty] | 7 | Cir. | Description |  | Amp | 8 | Cir. | Description |  | Amp | 9 | Cir. | Description |  | Amp |  |  | 1 |  | 11 |  | 1 |  | 11 |  | 1 |  | 11 |  | 1 |  | 11
[20 empty] | Found | 1 |  |  |  | Found | 1 |  |  |  | Found | 1 | [5 empty] | 2 |  | 12 |  | 2 |  | 12 |  | 2 |  | 12 |  | 2 |  | 12
7 | [19 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | 3 |  | 13 |  | 3 |  | 13 |  | 3 |  | 13 |  | 3 |  | 13
[20 empty] | Found | 2 |  |  |  | Found | 2 |  |  |  | Found | 2 | [5 empty] | 4 |  | 14 |  | 4 |  | 14 |  | 4 |  | 14 |  | 4 |  | 14
8 | [19 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | 5 |  | 15 |  | 5 |  | 15 |  | 5 |  | 15 |  | 5 |  | 15
[20 empty] | Found | 3 |  |  |  | Found | 3 |  |  |  | Found | 3 | [5 empty] | 6 |  | 16 |  | 6 |  | 16 |  | 6 |  | 16 |  | 6 |  | 16
9 | [19 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | 7 |  | 17 |  | 7 |  | 17 |  | 7 |  | 17 |  | 7 |  | 17
[20 empty] | Found | 4 |  |  |  | Found | 4 |  |  |  | Found | 4 | [5 empty] | 8 |  | 18 |  | 8 |  | 18 |  | 8 |  | 18 |  | 8 |  | 18
10 | [19 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | 9 |  | 19 |  | 9 |  | 19 |  | 9 |  | 19 |  | 9 |  | 19
[20 empty] | Found | 5 |  |  |  | Found | 5 |  |  |  | Found | 5 | [5 empty] | 10 |  | 20 |  | 10 |  | 20 |  | 10 |  | 20 |  | 10 |  | 20
11 | [19 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [8 empty] | Total | 0 |  |  | Total | 0 |  |  | Total | 0 |  |  | Total | 0
[20 empty] | Should equal rect. Amps |  |  | Total | 0 | Should equal rect. Amps |  |  | Total | 0 | Should equal rect. Amps |  |  | Total | 0 |  |  | Anode Junction Box |  |  |  | Anode Junction Box |  |  |  | Anode Junction Box |  |  |  | Anode Junction Box
12 | [19 empty] | Read # | Negative/Drains |  |  |  | Read # | Negative/Drains |  |  |  | Read # | Negative/Drains | [5 empty] | Date: |  |  |  | Date: |  |  |  | Date: |  |  |  | Date:
[20 empty] | 10 | Cir. | Description |  | Amp | 11 | Cir. | Description |  | Amp | 12 | Cir. | Description |  | Amp |  |  | Cir. | Amp | Cir. | Amp | Cir. | Amp | Cir. | Amp | Cir. | Amp | Cir. | Amp | Cir. | Amp | Cir. | Amp
| Day | Mo. | YR. |  | Remarks: | [12 empty] | More remarks Page 3 |  | Found | 1 |  |  |  | Found | 1 |  |  |  | Found | 1 | [5 empty] | 1 |  | 11 |  | 1 |  | 11 |  | 1 |  | 11 |  | 1 |  | 11
[20 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | 2 |  | 12 |  | 2 |  | 12 |  | 2 |  | 12 |  | 2 |  | 12
[20 empty] | Found | 2 |  |  |  | Found | 2 |  |  |  | Found | 2 | [5 empty] | 3 |  | 13 |  | 3 |  | 13 |  | 3 |  | 13 |  | 3 |  | 13
[20 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | 4 |  | 14 |  | 4 |  | 14 |  | 4 |  | 14 |  | 4 |  | 14
[20 empty] | Found | 3 |  |  |  | Found | 3 |  |  |  | Found | 3 | [5 empty] | 5 |  | 15 |  | 5 |  | 15 |  | 5 |  | 15 |  | 5 |  | 15
[20 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | 6 |  | 16 |  | 6 |  | 16 |  | 6 |  | 16 |  | 6 |  | 16
[20 empty] | Found | 4 |  |  |  | Found | 4 |  |  |  | Found | 4 | [5 empty] | 7 |  | 17 |  | 7 |  | 17 |  | 7 |  | 17 |  | 7 |  | 17
[20 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | 8 |  | 18 |  | 8 |  | 18 |  | 8 |  | 18 |  | 8 |  | 18
[20 empty] | Found | 5 |  |  |  | Found | 5 |  |  |  | Found | 5 | [5 empty] | 9 |  | 19 |  | 9 |  | 19 |  | 9 |  | 19 |  | 9 |  | 19
[20 empty] | Left |  |  |  |  | Left |  |  |  |  | Left | [6 empty] | 10 |  | 20 |  | 10 |  | 20 |  | 10 |  | 20 |  | 10 |  | 20
[20 empty] | Should equal rect. Amps |  |  | Total | 0 | Should equal rect. Amps |  |  | Total | 0 | Should equal rect. Amps |  |  | Total | 0 |  |  |  |  | Total | 0 |  |  | Total | 0 |  |  | Total | 0 |  |  | Total | 0
Note on H16: Power Company and phone number are useful in emergencies
Note on G17: Available at district or Midland offices This is optional and up to the district mgr.
Note on L17: Should be on power meter information plate
Note on R17: KWH reading taken only once per year during annual test point survey Note date in remarks at bottom of page. This is at the district Mgr's. descretion.
Note on B18: This is the rated voltage output for the rectifier
Note on G18: AC volts and Amps will typically be on the rectifier information plate and usually look like: 120/240VAC 50/25amps
Note on B19: This is the rated amperage output for the rectifier
Note on B21: Remote monitoring unit For future use
Note on B23: Anodes should be read individually at least once per year or prior to and immediately after the ground bed is watered. These can be recorded on page 3 of this form along with further instruction on watering procedures.
Note on U25: Never take a structure to soil reading from the negative lug on the rectifier. Find a nearby test point to use.
Note on K26: Separate drains/Individual negative leads should be recorded on the next page
Note on M26: Please pay particular attention to the rectifier/groundbed circuit resistance calculated in this column. When this value is equal to or greater than 2 ohms, your CP Technician or the Specialist should be notified by email. This might indicate the ground bed is deteriorating, drying out or that anodes are failing.
Note on A27: Please use same color data box on page 2 to record all individual negative/drains for structures serviced by this rectifier. If no adjustments were made, please use the darker rows for recording (as left).
Note on B27: Light shade row is for found readings Dark shade row is for left readings
Note on BH34: Anodes should be read once per year or if watered. Anode shunt size will be a .01 ohm or 50mV=5A Take DCmV reading and move the decimal point one place to the left and that will be your amp reading. Example: 23.15mV would be 2.315 amps
Note on BN34: Anodes should be read once per year or if watered. Anode shunt size will be a .01 ohm or 50mV=5A Take DCmV reading and move the decimal point one place to the left and that will be your amp reading. Example: 23.15mV would be 2.315 amps
Note on BT34: Anodes should be read once per year or if watered. Anode shunt size will be a .01 ohm or 50mV=5A Take DCmV reading and move the decimal point one place to the left and that will be your amp reading. Example: 23.15mV would be 2.315 amps
Note on BZ34: Anodes should be read once per year or if watered. Anode shunt size will be a .01 ohm or 50mV=5A Take DCmV reading and move the decimal point one place to the left and that will be your amp reading. Example: 23.15mV would be 2.315 amps
Note on BL47: This total should approximately equal the amperage output corresponding from page 1.
Note on BH48: Anodes should be read once per year or if watered. Anode shunt size will be a .01 ohm or 50mV=5A Take DCmV reading and move the decimal point one place to the left and that will be your amp reading. Example: 23.15mV would be 2.315 amps
Note on BN48: Anodes should be read once per year or if watered. Anode shunt size will be a .01 ohm or 50mV=5A Take DCmV reading and move the decimal point one place to the left and that will be your amp reading. Example: 23.15mV would be 2.315 amps
Note on BT48: Anodes should be read once per year or if watered. Anode shunt size will be a .01 ohm or 50mV=5A Take DCmV reading and move the decimal point one place to the left and that will be your amp reading. Example: 23.15mV would be 2.315 amps
Note on BZ48: Anodes should be read once per year or if watered. Anode shunt size will be a .01 ohm or 50mV=5A Take DCmV reading and move the decimal point one place to the left and that will be your amp reading. Example: 23.15mV would be 2.315 amps

## Rectifier J box illustration
POSITIVE LUG
RECTIFIER MAIN SHUNT
NEGATIVE LUG
METER PROBE LEADS | CIRCUIT BALANCE
+
-
AMPS
VOLTS
50mV=30A
25 AMPS
SQUARE D
SCOUT
ENERGY TRANSFER
DCP
WTG
Note on M8: ALWAYS HOOKED TO THE GROUND BED IS THE ANODIC SIDE OF THE CP CIRCUIT THIS SIDE CORRODES
Note on M11: RESIST THE TEMPTATION TO ASSUME THE POSITIVE SIDE OF THE SHUNT IS ON THE SAME PHYSICAL SIDE AS THE DC POSITIVE LUG. THIS IS NOT ALWAYS THE CASE TO DETERMINE THE CORRECT SIDE OF THE SHUNT TO PLACE YOUR POSITIVE METER LEAD PERFORM AS FOLLOWS: 1. PLACE THE RED METER LEAD ON THE POSITIVE LUG AND THE NEGATIVE LEAD ON THE NEGATIVE LUG. YOU SHOULD THEN OBSERVE THE METER POLARITY. (NO INDICATOR AS A PREFIX TO YOUR VOLT VALUE MEANS A POSITIVE READING. A NEGATIVE PREFIX INDICATES A NEGATIVE READING). IF YOU OBSERVE A NEGATIVE READING THEN TURN RECTIFIER OFF AND CALL A TECHNICIAN IF YOU ARE NOT THOROUGHLY TRAINED TO WORK ON THE UNIT. THIS INDICATES THAT THE UNIT IS MIS-WIRED AND YOUR ASSET IS THE ANODE. VERY IMPORTANT: THIS TEST SHOULD BE CONDUCTED EVERYTIME THE RECTIFIER IS READ. IT WILL VERIFY THE CORRECT POLARITY OF THE RECTIFIER 2. ASSUMING THE POLARITY IS CORRECT NOW PLACE THE TEST LEADS AT YOUR DISCRETION ON THE SHUNT TEST POINTS. IF THE READING IS NEGATIVE SIMPLY REVERSE THE LEADS AND YOU ARE CORRECTLY HOOKED UP. YOU SHOULD MARK THE CORRECT ATTACHMENT POSITION FOR FUTURE USE. 3. ALWAYS NOTE THE SHUNT VALUE AND USE THE SHUNT MULTIPLICATION FACTOR TO RECORD THE AMPERAGE READING.
Note on M14: ALWAYS ATTACHED TO THE PROTECTED STRUCTURE EITHER DIRECTLY OR THRU A MULTI-CIRCUIT J-BOX AS ILLUSTRATED IS THE CATHODIC SIDE OF THE CP CIRCUIT THIS SIDE IS PROTECTED
Note on B36: Red meter lead is always on the structure side Black meter lead is always on the current source side
Note on M36: BALANCING A MULTI-CIRCUIT NEGATIVE J-BOX CAN BE A VERY HARD PROCESS. IT IS BEST LEFT UP TO A TECHNICIAN WITH AMPLE TRAINING AND EXPERIENCE. THE GENERAL IDEA IS TO APPLY ENOUGH CURRENT TO MEET CRITERIA ON ALL AFFECTED STRUCTURES. SINCE THIS IS A SERIES/PARALLEL CIRCUIT, ANY RESISTANCE CHANGE TO ANY ONE CIRCUIT CHANGES THE AMPERAGE TO THE OTHER THREE. A VERY GOOD KNOWLEDGE OF CIRCUIT DYNAMICS IS NEEDED TO ACCOMPLISH THIS TASK. NEVER ATTEMPT ADJUSTMENT WITHOUT A REPRESENTATIVE FROM ALL STRUCTURE OWNERS AND A PROPERLY TRAINED TECHNICIAN PRESENT.

## WTGU Surface Ground bed design
|  | WTGU Surface Ground bed design |  |  | 2022-07-08
Farthest anode should be 300-350' from servicing pipeline if conditions permit
Anodes should be at least 15-20' apart (depending on count and space available)
Hole diameter will be 10-12" and at least 20' deep when possible
Each anode lead will be of sufficient length to reach the anode J-box. The j-box should
be located close to the rectifier or as on site conditions dictate.
The orientation of the bed will be perpendicular to the servicing pipeline.
Coke breeze to the top of the hole with Loresco RS-3
The bottom of each anode will be 3' off the bottom of the hole unless an identifiable
low resistance strata is located at a higher level.
Anode leads will be #8 HMWPE unless other is specified
Anode specification is for an Anotec cast iron 2684
Watering system will be schedule 40 3" PVC with 3" tee's at each hole with 3-4' down spouts
Watering procedure
Before applying water to the system, each anode needs to be read to establish
it's pre-water output. Leave your meter attached to the last anode (farthest from
the J-box). When this anode shows appreciative ouput increases then you know
that the water has reached the end. Now go ahead and read the rest of the anodes
to ensure that they have all received water. If not then keep the water flowing till
increases occur. Record the before and after on WTGU form 1200 and note the
amount of water used.
Caution: It is probably a good idea to tap the rectifer down prior to watering as the
lower total circuit resistance can become low eough to cause the rectifier to trip out
on over amperage. |  | Gravity feed the water only!
+
-
AMPS
VOLTS
50mV=30A
25 AMPS
5
3
2
1
4

## WTGU Deep Ground Bed Design
|  | Well Name | WTGU Standard deep well
Bore Diameter |  | 10" |  |  | Watering Pipe 3" PVC W/Female adaptor & plug
| 1 1/4" |  |  |  |  | Surface
| PVC |  |  |  | 3 ft.
vent pipe
1 1/4"
| All vent |  |  | 15 ft Bentonite
Hole Plug
Casing
Transition from allvent to PVC
Gravel
Depth
Gravel
| 350-400 | ft.
Total Well Depth
Coke Above Top Anode
[5 empty] | 20 | ft.
|  |  |  | Anodes qty. |  | 15-20
|  | Active |  | Anodes centers |  | 12'
Coke
Column
|  | 15-240' |  | Coke Backfill
|  | 20-270' |  |  | Type
Loresco SC-3 or approved
Coke Below Bottom Anode
[5 empty] | ~10 | ft.

## Select Options (hidden)
Amarillo | TX | 50mv5a=.1
Beaver | OK | 50mv10a=.2
Canadian | KS | 50mv15a=.3
Dalhart |  | 50mv20a=.4
Ft Stockton |  | 50mv25a=.5
Guymon |  | 50mv30a=.6
Hugoton |  | 50mv40a=.8
Junction |  | 50mv50a=1
Kermit |  | 50mv60a=1.2
Lubbock |  | 50mv75a=1.50
Other |  | 50mv120a=2.4
Pearsall |  | 50mv150a=3
Permian
Shamrock
Somerset
Stratford
Texhoma