## Form Details
| Gas Operations and Maintenance Manual |  | Form WTG-1202 Atmospheric Corrosion Survey Rev 2 - January 2022
When to Use This Form | This form packet is used to document inspection of pipelines that are exposed to the atmosphere.
Reviewed Procedures | P-192.479 Protection Against Atmospheric Corrosion
P-192.481 Visually Inspect for Atmospheric Corrosion
The applicable sections of the above procedure(s) shall be reviewed prior to completing this form.
Documentation Procedure
| 1. | Copy this form and return original to manual.
| 2. | Refer to Corrosion Control Procedures in the O&M Manual to ensure inspections are done correctly.
| 3. | Gather data and complete form.
| 4. | If corrosion is found or there is a suspected need for remediation, document below and forward this document to the Corrosion Control Engineer for immediate review.
| 5. | Place completed form in file. Retain records for the life of the pipeline system.
Form Version | Rev 2 - January 2022

## WTG-1202
Form WTG-1202 Atmospheric Corrosion Survey Rev 2 - January 2022
Gas Operations and Maintenance Manual
Survey Year: |  |  |  | District:
Facility Type: |  |  |  |  | TRC/CC Unit
System Type: |  |  | Latitude |  |  | Longitude
Facility Description:
System:
Line Segment:
Examine facility piping for corrosion
Corrosion found? |  |  | Non-destructive testing performed?
Comments/Description:
Air to soil interface coating condition: |  |  | Comments/Description Below:
Support structures, fence and building coating condition: |  |  |  |  | Comments/Description Below:
Corrosion under clamps or between pipe and saddle |  |  |  | Are pipe supports mechanically stable?
Comments/Description:
Paint Condition?
If pitting was found, were the Specialist and Supervisor notified:
Please record any observations:
Remedial Actions required? |  | If Yes, provide description below:
Date Remedial Actions completed: |  |  |  | Signature:
Inspector's Signature: | [5 empty] | Date:
Note on B14: Refer to WTG O&M P_192.481 Visually inspect for Atmospheric Corrosion
Note on B16: Inspect all above ground piping and if shown evidence of corrosion damage or other conditions warrant, conduct non-destructive testing. Use the comments to identify methods used.
Note on B20: Inspect the soil/air interfaces or transition zone of pipe entering the ground or water to confirm that it is properly coated to prevent penetration of water between the pipe and the coating. Ensure special attention is paid to areas under thermal disbonded coating, pipe supports, splash zones, deck penetrations and spans over water. If a condition is observed where moisture may be retained between the coating and pipe, remove the coating, inspect the pipe, evaluate the severity of any present corrosion, take remedial action (procedure P-192.483) and recoat the pipe prior to the next inspection. (see procedure P-192.461 or P-192.479) Issue a repair order F-192.709 to handle any required repairs.

## Example Form
Form WTG-1202 Atmospheric Corrosion Survey Rev 2 - January 2022
Survey Year: | 2022 |  |  |  | District: |  | Guymon
Facility Type: | AGL Valve |  |  |  |  | TRC/CC Unit |  | xxxx
System Type: | Transmission |  |  | Latitude | 36.3333 |  | Longitude | -101.6333
Facility Description: | AGL Valve south side of old Goodwell, OK golf course
System: | WTG/WGI East
Line Segment: | East Main line Goodwell C-3
Examine facility piping for corrosion
Corrosion found? |  | Yes |  | Non-destructive testing performed? |  |  |  | No
Comments/Description:
Old localized pitting at 3 o'clock position next to the weld on the West valve flange.
Air to soil interface coating condition: |  |  | Good | Comments/Description Below:
Support structures, fence and building coating condition: |  |  |  |  | Good | Comments/Description Below:
Guard is in good condition with fresh paint job
Corrosion under clamps or between pipe and saddle |  |  |  | N/A | Are pipe supports mechanically stable? |  |  |  | N/A
Comments/Description:
N/A
Paint Condition? |  |  | Good
If pitting was found, were the Specialist and Supervisor notified: | [5 empty] | No
Please record any observations:
The minor pitting will be cleaned and touched up.
Remedial Actions required? |  | Yes | If Yes, provide description below:
See above comments
Date Remedial Actions completed: |  |  | 2022-02-12 |  | Signature: | Johnny Appleseed
Inspector's Signature: |  | Johnny Appleseed |  |  |  |  | Date: | 2022-02-07
Note on A14: Refer to WTG O&M P_192.481 Visually inspect for Atmospheric Corrosion
Note on A16: Inspect all above ground piping and if shown evidence of corrosion damage or other conditions warrant, conduct non-destructive testing. Use the comments to identify methods used.
Note on A20: Inspect the soil/air interfaces or transition zone of pipe entering the ground or water to confirm that it is properly coated to prevent penetration of water between the pipe and the coating. Ensure special attention is paid to areas under thermal disbonded coating, pipe supports, splash zones, deck penetrations and spans over water. If a condition is observed where moisture may be retained between the coating and pipe, remove the coating, inspect the pipe, evaluate the severity of any present corrosion, take remedial action (procedure P-192.483) and recoat the pipe prior to the next inspection. (see procedure P-192.461 or P-192.479) Issue a repair order F-192.709 to handle any required repairs.

## Select Options (hidden)
Amarillo | 2021 | Transmission | Active
Beaver | 2022 | Distribution | Existing
Canadian | 2023 | Gathering
Dalhart | 2024
Ft Stockton | 2025
Guymon | 2026
Hugoton | 2027 | Yes | Good
Junction | 2028 | No | Fair
Kermit | 2029 | N/A | Poor
Lubbock | 2030
Other | 2031
Pearsall
Permian
Shamrock
Somerset | AGL Valve
Stratford | Compressor
Texhoma | Mtr. Riser
Reg/Mtr Sta.
Trap
Vault Valve